|  | FACTSHEET 04/01a ECP16000s Technical Specification |
| --- | --- |

| Producing a flow rate of up to 16,000m3/hr this evaporative cooler is manufactured by EcoCooling Limited in an ISO 9002 quality environment. Designed to meet all European electrical, water and other safety legislation. CABINET: The cabinet components are injection moulded structural foam polypropylene. The cabinets are UV stabilised and corrosion free. The fan housing is manufactured from stainless steel. COOLING PADS: Cooling pads are Munters Celdek honeycomb, saturation efficiencies in the range of 85-89 % Munters CelDek 680x850x100mm, three pads total area 1.8m2 |  |
| --- | --- |
| MOTOR: FAN MOTORS: Variable; Two Speed. Motor Type; EVA - VS; EVA - VS. Poles; 4; 6/12. Speed; 1340rpm; 940/600 rpm. Volts; 220V AC; 220V AC. Hz; 50; 50. Amps Start; 12A; 8A. Amps Run; 8A; 5.6/3.5 A. Capacitor; 60F/450V; 30F/450V. Duty; S1; S1. Ins; F; F. IP; 44; 44. Overload; Auto Reset; Auto Reset. |  |

WATER: Supply minimum 1 bar max 7 bar.  Minimum supply 500 L/hr. Sump Capacity 23L

ELECTRICAL SUPPLY:  240V 50Hz.  10A start 5A running

DRAIN: Minimum capacity 2000l/hr to an appropriate effluent point in accordance with local water regulations.

CIRCULATION PUMP: 50W, 30L/min, Centrifugal, Encapsulated, Shaded Pole Magnetically Coupled, Auto reset overload.

DIMENSIONS: Height 950mm, Length 1170mm Width 1170mm, Volume 1.3m3

WEIGHT:   Dry 55Kg Operating 92kg.  The cooler is designed to be supported from a plain edged vertical duct.

DUCT: Length 645mm x Width 645mm

CONTROL:  Can be controlled in groups:  Facility to directly connect to timer, thermostat, internal humidistat, external humidistat and fire alarm contact.

Refer to separate documentation for details.

OPTIONAL EXTRAS:

Weather seal:  Automatically shuts air flow when fan is stopped

WARRANTY:  Two years: parts only.

Always refer to the website www.ecocooling.org  for latest specifications